Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

R3.4.5

SERIES: EWHQ~G-

GENERAL CHARACTERISTICS

Electronic expansion valve The unit is equipped with the most advanced electronic expansion valves to achieve precise control of refrigerant mass flow. As today’s system requires improved energy efficiency, tighter temperature control, wider range of operating conditions and incorporate features like remote monitoring and diagnostics, the application of electronic expansion valves becomes mandatory.

Electronic expansion valves possess unique features: short opening and closing time, high resolution, positive shut-off function to eliminate use of additional solenoid valve, continuous modulation of mass flow without stress in the refrigerant circuit and corrosion resistance stainless steel body.

Electronic expansion valves are typically working with lower ΔP between high and low pressure side, than a thermostatic expansion valve. The electronic expansion valve allows the system to work with low condenser pressure without any refrigerant flow problems and with a perfect chilled water leaving temperature control.

Refrigerant Units have been optimized to operate with R-410A, refrigerant with zero ODP (Ozone Depletion Potential) and GWP (Global Warming Potential) 1890. R-410A has been the logical choice for our multiple scroll chiller because today it is one of the most promising refrigerants in terms of efficiency, stability and environmental impact. R-410A offers a small swept volume, a good heat exchange capacity and leads to reduced component sizes of items such as heat exchangers and tubing.

Compressor The compressor is hermetic orbiting scroll compressor complete with motor over-temperature and over-current devices. An oil heater, which starts automatically, keeps the oil from being diluted by the refrigerant when the compressor stops. The compressors are connected in Tandem on a single refrigerating circuit and are fitted on rubber antivibration mounts and complete with oil charge.

Cabinet and structure The cabinet is made of galvanized steel sheet and painted to provide a high resistance to corrosion. Colour Ivory White (Munsell code 5Y7.5/1) (±RAL7044).The base frame has an eye-hook to lift the unit with ropes for an easy installation. The weight is uniformly distributed along the profiles of the base and this facilitates the arrangement of the unit.

Page 1 of 6

Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

Source side exchanger The unit is equipped with a reversible direct expansion plate to plate type exchanger. This heat exchanger is made of stainless steel brazed plates and is covered with a 20mm closed cell insulation material. The exchanger is manufactured in accordance to PED approval. Flow switch and victaulic kit are provided mounted as option.

Refrigerant circuit Each unit has 1 circuit, according to the capacity, that includes:

• Compressors

• Refrigerant

• Evaporator

• Condenser

• 4 ways valve

• Electronic expansion valve

• High pressure switch

• High pressure transducers

• Low pressure transducers

• Suction temperature sensor

Electrical control panel Power and control are located in the main panel. The electrical panel is IP54 and (when opening the doors) internally protected with plexiglass panel against possible accidental contact with electrical components (IP20). The main panel is fitted with a main switch interlocked door.

Power Section

The power section includes compressors protection devices, compressors starters and control circuit power supply.

Unit controller

Unit controller is installed as standard; it can be used to modify unit set-points and check control parameters. A built-in display shows chiller operating status plus temperatures and pressures of water, refrigerant, programmable values, set-points. A sophisticated software with predictive logic, selects the most energy efficient combination of compressors and EEXV to keep stable operating conditions to maximise chiller energy efficiency and reliability.

The unit controller is able to protect critical components based on external signs from its system (such as motor temperatures, refrigerant gas and oil pressures, correct phase sequence, pressure switches and evaporator). The input coming from the high pressure switch cuts all digital output from the controller in less than 50ms, this is an additional security for the equipment.

Fast program cycle (200ms) for a precise monitoring of the system. Floating point calculations supported for increased accuracy in Pressure / Temperature conversions.

Control section - main features

Control Section has the following feature.

• Management of the refrigerant circuit capacity

• Full routine operation at condition of:

- high thermal load

- high evaporator entering water temperature (start-up)

• Display of evaporator entering/leaving water temperature.

•Display of condensing-evaporating temperature and pressure, suction superheat for each circuit.

• Compressor and pumps hours counter.

• Display of Status Safety Devices.

• Number of starts and compressor working hours.

• Optimized management of compressor load.

• Re-start in case of power failure (automatic / manual).

• Soft Load (optimized management of the compressor load during the start-up).

• Start at high evaporator water temperature.

• Return Reset (Set Point Reset based on return water temperature).

• Set point Reset (optional).

• Application and system upgrade with commercial SD cards.

• Ethernet port for remote or local servicing using standard web browsers.

• Two different sets of default parameters could be stored for easy restore.

Page 2 of 6

Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

Safety device / logic for each refrigerant circuit

The following devices / logics are available.

• High pressure (pressure switch).

• High pressure (transducer).

• Low pressure (transducer).

• High motor winding temperature.

• Low pressureratio.

• No pressure change at start

System security

The following securities are available.

• Phase monitor.

• Freeze protection.

Regulation type

Proportional + integral + derivative regulation on the evaporator leaving water output probe.

Unit controller

Unit controller built-in terminal has the following features.

• 164x44 dots liquid crystal display with white back lighting. Supports Unicode fonts for multi-lingual.

• Key-pad consisting of 3 keys.

• Push’n’Roll control for an increased usability.

• Memory to protect the data.

• General faults alarm relays.

• Password access to modify the setting.

• Application security to prevent application tampering or hardware usability with third party applications.

• Service report displaying all running hours and general conditions.

• Alarm history memory to allow an easy fault analysis.

User side exchanger The unit is equipped with a reversible direct expansion plate to plate type exchanger. This heat exchanger is made of stainless steel brazed plates and is covered with a 20mm closed cell insulation material. The exchanger is manufactured in accordance to PED approval. Flow switch and victaulic kit are provided mounted as option.

Additional information related to F-GAS Regulation (EU) No 517/2014 OF THE European Parliament and of the Council of 16 April 2014 on fluorinated greenhouse gases and repealing Regulation (EC) No 842/2006

Page 3 of 6

Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

TECHNICAL SPECIFICATIONS (data referred to EN14511)

EWHQ120G-SS

MODEL

95,1

Capacity - Cooling

kW

Step

Capacity control - Type

28,7

Unit power input - Cooling

kW

3,31

EER

4,57

ESEER

5,75

IPLV

CASING

IW

Colour *

GPSS

Material *

DIMENSIONS

1066

Height

mm

928

Width

mm

2432

Length

mm

WEIGHT

608

Unit Weight

kg

654

Operating Weight

kg

WATER HEAT EXCHANGER (Evaporator)

PHE

Type *

Ethylene Glycol 20%

Fluid

0,0000176

Fouling factor

m² °C/W

8

Water Volume

l

14,0/8,0

Water temperature (in/out)

°C

4,0

Nominal water flow rate - Cooling

l/s

32

Nominal Water pressure drop - Cooling **

kPa

CC

Insulation material *

WATER HEAT EXCHANGER (Condenser)

PHE

Type *

Water

Fluid

0,0000440

Fouling factor

m² °C/W

8

Water Volume

l

35,0/40,0

Water temperature (in/out)

°C

6,0

Nominal water flow rate - Cooling

l/s

68

Nominal Water pressure drop - Cooling **

kPa

COMPRESSOR

Scroll

Type

8

Oil charge

l

2

Quantity

No.

SOUND LEVEL

83

Sound Power - Cooling***

dB(A)

67

Sound Pressure - Cooling

dB(A)

REFRIGERANT CIRCUIT

R410A

Refrigerant type

9

Refrigerant charge

kg

1

N. of circuits

No.

PIPING CONNECTIONS

1" 1/2

Evaporator water inlet/outlet

1" 1/2

Condenser water inlet/outlet

* IW: Ivory White - GPSS: Galvanized and Painted Steel Sheet - PHE: Plate Heat Exchanger - S&T: Single Pass Shell & Tube.* CC: Closed Cell - HFP: High efficiency fin and tube type - DPT: Direct Propeller Type - DOL: Direct On Line - VFD: Inverter - BRS: Brushless.** If red contact factory.***sound power level (@STD conditions) are mesuared in accordance with ISO 9614 and Eurovent 8/1 for Eurovent certified units

Page 4 of 6

Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

TECHNICAL SPECIFICATIONS - HEATING MODE

MODEL

EWHQ120G-SS

129

kW

Capacity - Heating *

29,2

kW

Unit power input - Heating *

4,42

---

COP *

95,1

kW

Capacity - Cooling *

HEAT EXCHANGER - EVAPORATOR

5,1

l/s

Nominal water flow rate

51

kPa

Nominal Water pressure drop

HEAT EXCHANGER - CONDENSER

6,2

l/s

Nominal water flow rate

74

kPa

Nominal Water pressure drop

Fluid: Ethylene Glycol

*  Heating capacity, unit power input and COP are based on the following conditions: evaporator 5,0/10,0°C; condenser 35,0/40,0 °C, unit at full load operation;

PARTIAL HEAT RECOVERY MODE (Heat Recovery ON)

MODEL

EWHQ120G-SS

96,7

kW

Capacity - Cooling

27,0

kW

Unit power input - Cooling

31,4

kW

Heat recovery capacity

4,74

TEER (Total Energy Efficiency Ratio)

HEAT RECOVERY EXCHANGER

PHE

Type

40,0

°C

Water temperature in

45,0

°C

Water temperature out

1,5

l/s

Nominal water flow rate

10

kPa

Nominal Water pressure drop

EVAPORATOR

4,1

l/s

Nominal water flow rate

33

kPa

Nominal Water pressure drop

Page 5 of 6

Chiller selection software

Printing date: 2016/03/24

DAIKIN

CSS - Rev. 9.4

ELECTRICAL SPECIFICATIONS

EWHQ120G-SS

MODEL

Power supply

3

No.

Phases

50

Hz

Frequency

400

V

Voltage

-10%

%

Voltage tolerance Minimum

+10%

%

Voltage tolerance Maximum

Unit

255

A

Maximum starting current

47

A

Nominal running current cooling

66

A

Maximum running current

72

A

Maximum current for wires sizing

51

A

Running current (1)

Compressors

3

Hz

Phases

400

V

Voltage

-10%

%

Voltage tolerance Minimum

+10%

%

Voltage tolerance Maximum

66

A

Maximum running current

DOL

Starting method

Fluid:  + Ethylene Glycol 20%

Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.

Maximum starting current: starting current of biggest compressor + current of the compressor at 75% maximum load

Nominal current in cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C

Maximum running current is based on max compressor absorbed current in its envelope

Maximum unit current for wires sizing is based on minimum allowed voltage

Maximum current for wires sizing: (compressors full load ampere) x 1,1.

(1) Running current based on the following conditions: evaporator 14,0/8,0°C;  condenser 35,0/40,0 °C

SOUND LEVELS

Sound pressure level at 1 m from the unit (rif. 2 x 10-5 Pa)

Power

63 Hz

125 Hz

250 Hz

8000 Hz

dB(A)

dB(A)

500 Hz

1000 Hz

MODEL

2000 Hz

4000 Hz

EWHQ120G-SS

64,4

60,3

63,1

54,5

60,3

83,0

62,4

58,6

67,0

49,1

Fluid:  + Ethylene Glycol 20%

Note: The values are according to ISO 3744 and are referred to: evaporator 12/7 °C, condenser 30/35 °C, full load operation

Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are mesuared in accordance with ISO 9614

and Eurovent 8/1 for Eurovent certified units.

The certification refers only to the overall sound power level, the sound pressure is calculated from the sound power level and are

for information only and not cosidered bounding

Page 6 of 6